## Frese S
QUICK - CALC Frese S
Setting & Selection program Frese S Dynamic Balancing Valve
Input
Eingabe dP = | 20 | (kPa) Differenzdruck am Ventil
Input Q = | 1200 | (l/h) Flow
Dimension | Range |  | Calculation
| Flow (l/h) | Range ∆Pp (kPa) | Pre-set | Kv | Min. ∆P (kPa)
DN15 LP | 25-804 | 8-250 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN15 HP | 40-1100 | 16-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN20 LP | 41-1265 | 9-250 | 9.0101 | 3.1677 | 14.3508
DN20 HP | 66-1850 | 12-400 | 6.7839 | 2.6336 | 20.7622
DN25 LP | 61-1663 | 9-250 | 6.4402 | 3.1622 | 14.4003
DN25 HP | 89-2350 | 12-400 | 4.8698 | 2.7192 | 19.4744
DN32 | 217-4800 | 14-400 | 2.9228 | 2.8834 | 17.3203
DN40 | 175-7450 | 15-400 | 2.4488 | 2.9042 | 17.0726
DN50 | 440-10350 | 17-400 | 1.6696 | 2.809 | 18.2498
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN
Type |  |  | X | Y | Z | Kvs | Min | Max | Evaluering af Flow | Evaluering af Dp
DN15 LP | [5 empty] | 2.2 | 25 | 804 | UDEN FOR OMRÅDET | 20
DN15 HP | [5 empty] | 2.4 | 40 | 1100 | UDEN FOR OMRÅDET | 20
DN20 LP | [5 empty] | 3.3 | 41 | 1265 | 1200 | 20
DN20 HP | [5 empty] | 3.6 | 66 | 1850 | 1200 | 20
DN25 LP | [5 empty] | 4.1 | 61 | 1663 | 1200 | 20
DN25 HP | [5 empty] | 4.4 | 89 | 2350 | 1200 | 20
DN32 | [5 empty] | 8.8 | 217 | 4800 | 1200 | 20
DN40 | [5 empty] | 13.2 | 175 | 7450 | 1200 | 20
DN50 | [5 empty] | 16.7 | 440 | 10350 | 1200 | 20

## Frese SIGMA Compact
QUICK - CALC Frese SIGMA Compact
Setting & Selection program Frese SIGMA Compact Dynamic Balancing Valve
Eingabe dP = | 20 | (kPa) Differenzdruck am Ventil
Input Q = | 137 | (l/h) Flow
Dimension | Range |  | Calculation
| Flow (l/h) | Range ∆Pp (kPa) | Pre-set | Kv | Min. ∆P (kPa)
DN15 Low | 40-900 | 10-400 | 0.77825 | 0.069744 | 10.1103
DN15 High | 60-1080 | 14-400 | 0.7 | 0.053013 | 13.9819
DN20 Low | 86-1550 | 9-400 | 0.57124 | 0.082252 | 8.9769
DN20 High | 102-1930 | 16-400 | 0.5 | 0.092524 | 16
DN25 Low | 38-900 | 10-400 | 0.9 |  | 10
DN25 High | 137-2400 | 14-400 | 0.5 | 0.089461 | 14
DN32 | 200-5000 | 15-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN40 | 719-7400 | 10-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN50 | 900-10350 | 10-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN
Type |  |  | X | Y | Z | Kvs | Min | Max | Evaluering af Flow | Evaluering af Dp
DN15 LF | [5 empty] | 2.6 | 40 | 900 | 137 | 20
DN15 HF | [5 empty] | 2.6 | 60 | 1080 | 137 | 20
DN20 LF | [5 empty] | 4 | 86 | 1550 | 137 | 20
DN20 HF | [5 empty] | 4 | 102 | 1930 | 137 | 20
DN25 LF | [5 empty] | 2.3 | 38 | 900 | 137 | 20
DN25 HF | [5 empty] | 4.2 | 137 | 2400 | 137 | 20
DN32 | [5 empty] | 10.9 | 200 | 5000 | UDEN FOR OMRÅDET | 20
DN40 | [5 empty] | 18 | 719 | 7400 | UDEN FOR OMRÅDET | 20
DN50 | [5 empty] | 20.3 | 900 | 10350 | UDEN FOR OMRÅDET | 20

## Frese OPTIMA
QUICK - CALC Frese OPTIMA
Setting & Selection program Frese OPTIMA Pressure Independent Control Valve
Input
Eingabe dP = | 20 | (kPa) Differenzdruck am Ventil
Input Q = | 2204 | (l/h) Flow
Dimension | Range |  | Calculation
| Flow (l/h) | Range ∆Pp(kPa) | Pre-set | Kv | Min. ∆P (kPa)
DN15 LF | 78-625 | 14-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN15 HF | 244-1724 | 14-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN20 LF | 131-1050 | 14-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN20 HF | 292-2039 | 13-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN25 LF | 231-1722 | 14-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN25 HF | 292-2039 | 14-400 | NOT POSSIBLE | #VALUE! | NOT POSSIBLE
DN32 | 465-3056 | 14-400 | 2.464 | 5.4061 | 16.6207
DN40 | 2022-7105 | 16-400 | 0.54367 | 5.421 | 16.5296
DN50 | 2204-8586 | 19-400 | 0.51234 | 5.2201 | 19
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN
Type |  |  | X | Y | Z | Kvs | Min | Max | Evaluering af Flow | Evaluering af Dp
DN15 LF | [5 empty] | 1.6 | 78 | 625 | UDEN FOR OMRÅDET | 20
DN15 HF | [5 empty] | 4.1 | 244 | 1724 | UDEN FOR OMRÅDET | 20
DN20 LF | [5 empty] | 2.6 | 131 | 1050 | UDEN FOR OMRÅDET | 20
DN20 HF | [5 empty] | 4.3 | 292 | 2039 | UDEN FOR OMRÅDET | 20
DN25 LF | [5 empty] | 4.3 | 231 | 1722 | UDEN FOR OMRÅDET | 20
DN25 HF | [5 empty] | 4.3 | 292 | 2039 | UDEN FOR OMRÅDET | 20
DN32 | [5 empty] | 7.2 | 465 | 3056 | 2204 | 20
DN40 | [5 empty] | 13.9 | 2022 | 7105 | 2204 | 20
DN50 | [5 empty] | 15.2 | 2204 | 8586 | 2204 | 20

## Frese OPTIMA Compact
QUICK - CALC Frese OPTIMA Compact
Setting & Selection program Frese OPTIMA Compact Pressure Independent Control Valve
Input
Eingabe dP = | 20 | (kPa) Differenzdruck am Ventil
Input Q = | 1000 | (l/h) Flow
Dimension | Range |  | Calculation
| Flow (l/h) | Range ∆Pp(kPa) | Pre-set | Min. ∆P (kPa)
DN10 Low 2,5 | 30-200 | 14-400 | NOT POSSIBLE | NOT POSSIBLE
DN10 Low 5,0 | 65-370 | 14-400 | NOT POSSIBLE | NOT POSSIBLE
DN15 Low 2,5 | 30-200 | 14-400 | NOT POSSIBLE | NOT POSSIBLE
DN15 Low 5,0 | 65-370 | 14-400 | NOT POSSIBLE | NOT POSSIBLE
DN15 High 2,5 | 100-575 | 15-400 | NOT POSSIBLE | NOT POSSIBLE
DN15 High 5,0 | 220-1330 | 16-400 | 3.0261 | 20.682
DN20 High 2,5 | 100-575 | 15-400 | NOT POSSIBLE | NOT POSSIBLE
DN20 High 4,0 | 160-990 | 15-400 | NOT POSSIBLE | NOT POSSIBLE
DN20 High 5,0 | 220-1330 | 16-400 | 3.0261 | 20.682
DN20 High 5,5 | 300-1800 | 18-400 | 2.4 | 24.1914
DN25 Low 5,5 | 280-1800 | 15-400 | 2.5 | 20.2197
DN25L High 5,5 | 600-3609 | 17-400 | 1.052 | 17.4491
DN32 | 550-4001 | 18-400 | 1.0431 | 18.1599
DN40 | 1370-9500 | 10-400 | NOT POSSIBLE | NOT POSSIBLE
DN50 | 1400-11500 | 10-400 | NOT POSSIBLE | NOT POSSIBLE
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
Type |  |  | X | Z | Kvs | Min | Max | Evaluering af Flow | Evaluering af Dp
DN10 Low 2,5 |  |  |  |  | 0.5 | 30 | 200 | UDEN FOR OMRÅDET | 20
DN10 Low 5,0 |  |  |  |  | 0.9 | 65 | 370 | UDEN FOR OMRÅDET | 20
DN15 Low 2,5 |  |  |  |  | 0.5 | 30 | 200 | UDEN FOR OMRÅDET | 20
DN15 Low 5,0 |  |  |  |  | 0.9 | 65 | 370 | UDEN FOR OMRÅDET | 20
DN15 High 2,5 |  |  |  |  | 1.3 | 100 | 575 | UDEN FOR OMRÅDET | 20
DN15 High 5,0 |  |  |  |  | 2.7 | 220 | 1330 | 1000 | 20
DN20 High 2,5 |  |  |  |  | 1.3 | 100 | 575 | UDEN FOR OMRÅDET | 20
DN20 High 4,0 |  |  |  |  | 2.1 | 160 | 990 | UDEN FOR OMRÅDET | 20
DN20 High 5,0 |  |  |  |  | 2.7 | 220 | 1330 | 1000 | 20
DN20 High 5,5 |  |  |  |  | 2.9 | 300 | 1800 | 1000 | 20
DN25 Low 5,5 |  |  |  |  | 2.9 | 280 | 1800 | 1000 | 20
DN25L High 5,5 |  |  |  |  | 7.5 | 600 | 3609 | 1000 | 20
DN32 |  |  |  |  | 7.6 | 550 | 4001 | 1000 | 20
DN40 |  |  |  |  | 19 | 1370 | 9500 | UDEN FOR OMRÅDET | 20
DN50 |  |  |  |  | 19 | 1400 | 11500 | UDEN FOR OMRÅDET | 20

## Frese OPTIMA Compact Flanged
QUICK - CALC Frese OPTIMA Flanged
Setting & Selection program Frese OPTIMA Flanged Pressure Independent Control Valve
Input
Eingabe dP = | 20 | (kPa) Differenzdruck am Ventil
Input Q = | 280 | (m3/h) Flow
Dimension | Range |  | Calculation
| Flow (m3/h) | Range ∆Pp(kPa) | Pre-set | Min. ∆P (kPa)
DN50 Low Flow | 2,48-15,00 | 7-600 | NOT POSSIBLE | NOT POSSIBLE
DN50 High Flow | 3,92-24,00 | 19-600 | NOT POSSIBLE | NOT POSSIBLE
DN65 Low Flow | 4,38-25,00 | 15-600 | NOT POSSIBLE | NOT POSSIBLE
DN65 High Flow | 5,95-35,00 | 30-600 | NOT POSSIBLE | NOT POSSIBLE
DN80 Low Flow | 5,34-34,00 | 16-600 | NOT POSSIBLE | NOT POSSIBLE
DN80 High Flow | 7,02-43,00 | 23-600 | NOT POSSIBLE | NOT POSSIBLE
DN100 Low Flow | 12,10-68,00 | 20-600 | NOT POSSIBLE | NOT POSSIBLE
DN100 High Flow | 14,80-90,00 | 30-600 | NOT POSSIBLE | NOT POSSIBLE
DN125 Low Flow | 18.5-110.0 | 16-600 | NOT POSSIBLE | NOT POSSIBLE
DN125 High Flow | 23.0-135.0 | 27-600 | NOT POSSIBLE | NOT POSSIBLE
DN150 Low Flow | 25.6-148.0 | 21-600 | NOT POSSIBLE | NOT POSSIBLE
DN150 High Flow | 32.0-195.0 | 33-600 | NOT POSSIBLE | NOT POSSIBLE
DN200 Low Flow | 25.6-148.1 | 21-601 | NOT POSSIBLE | NOT POSSIBLE
DN200 High Flow | 32.0-195.1 | 33-601 | 4.0005 | 78.0061
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN
Type |  |  | X | Z | Kvs | Min | Max | Evaluering af Flow
DN50 Low Flow |  |  |  |  | 33.5 | 2.48 | 15 | UDEN FOR OMRÅDET
DN50 High Flow |  |  |  |  | 33.5 | 3.92 | 24 | UDEN FOR OMRÅDET
DN65 Low Flow |  |  |  |  | 50 | 4.38 | 25 | UDEN FOR OMRÅDET
DN65 High Flow |  |  |  |  | 50 | 5.95 | 35 | UDEN FOR OMRÅDET
DN80 Low Flow |  |  |  |  | 68 | 5.3 | 34 | UDEN FOR OMRÅDET
DN80 High Flow |  |  |  |  | 68 | 7 | 43 | UDEN FOR OMRÅDET
DN100 Low Flow |  |  |  |  | 115 | 12.1 | 68 | UDEN FOR OMRÅDET
DN100 High Flow |  |  |  |  | 115 | 14.8 | 90 | UDEN FOR OMRÅDET
DN125 Low Flow |  |  |  |  | 167 | 18.5 | 110 | UDEN FOR OMRÅDET
DN125 High Flow |  |  |  |  | 167 | 23 | 135 | UDEN FOR OMRÅDET
DN150 Low Flow |  |  |  |  | 250 | 25.6 | 148 | UDEN FOR OMRÅDET
DN150 High Flow |  |  |  |  | 241.9 | 32 | 195 | UDEN FOR OMRÅDET
DN200 Low Flow |  |  |  |  | 371 | 95 | 210 | UDEN FOR OMRÅDET
DN200 High Flow |  |  |  |  | 317 | 130 | 280 | 280

## Frese PV
QUICK - CALC Frese PV
Setting & Selection program Frese PV Differential Pressure Control Valve
Input
Input ∆Ps = |  | 40 | (kPa) Differential Pessure setting
Input Q = |  | 15000 | (l/h) Design flow
Dim. | ∆Ps range | Range |  | Pre-set
|  | Flow (l/h) | Range ∆Pp (kPa) | Number of turns
DN15 | 5-30 kPa | 50-600 | 5-400 | NOT POSSIBLE
DN15 | 20-60 kPa | 100-1200 | 20-400 | NOT POSSIBLE
DN20 | 5-30kPa | 100-1000 | 5-400 | NOT POSSIBLE
DN20 | 20-60kPa | 150-2000 | 20-400 | NOT POSSIBLE
DN25 | 5-30 kPa | 600-2500 | 5-400 | NOT POSSIBLE
DN25 | 20-60 kPa | 700-4000 | 20-400 | NOT POSSIBLE
DN32 | 20-80 kPa | 1000-5000 | 20-400 | NOT POSSIBLE
DN40 | 20-80 kPa | 3000-8000 | 20-400 | NOT POSSIBLE
DN50 | 20-80 kPa | 5000-15000 | 20-400 | 13.3532
Calculation of pressure loss
Dimension |  | ∆Pv (kPa) | Min. ∆Pp (kPa)
DN15 5-30 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN15 20-60 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN20 5-30kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN20 20-60kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN25 5-30 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN25 20-60 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN32 20-80 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN40 20-80 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN50 20-80 kPa |  | 70.2225 | 110.2225
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN
Type |  | X | Y | Z | Kvs | Min | Max | Evaluering af Flow | Evaluering af Dp
DN15 5-30 kPa |  | 5 | 494.76 | 0.5575 | 3.6 | 50 | 600 | UDEN FOR OMRÅDET | UDEN FOR OMRÅDET
DN15 20-60 kPa |  | 20 | 747.59 | 0.3133 | 3.6 | 100 | 1200 | UDEN FOR OMRÅDET | 40
DN20 5-30 kPa |  | 5 | 682.82 | 0.59 | 4 | 100 | 1000 | UDEN FOR OMRÅDET | UDEN FOR OMRÅDET
DN20 20-60 kPa |  | 20 | 596.44 | 0.324 | 4 | 150 | 2000 | UDEN FOR OMRÅDET | 40
DN25 5-30 kPa |  | 5 | 802.65 | 1.26 | 9.5 | 600 | 2500 | UDEN FOR OMRÅDET | UDEN FOR OMRÅDET
DN25 20-60 kPa |  | 20 | 1529.6 | 0.7175 | 9.5 | 700 | 4200 | UDEN FOR OMRÅDET | 40
DN32 20-80 kPa |  | 20 | 1338.84 | 0.4833 | 11.4 | 1000 | 5000 | UDEN FOR OMRÅDET | 40
DN40 20-80 kPa |  | 20 | 2213.08 | 0.4133 | 16.4 | 3000 | 8000 | UDEN FOR OMRÅDET | 40
DN50 20-80 kPa |  | 20 | 2234.42 | 0.352 | 17.9 | 5000 | 15000 | 15000 | 40
∆Pp = Pump pressure
∆Ps = Differential pressure setting
∆Pv = Pressure loss across valve
∆Pp = Pump pressure
∆Ps = Differential pressure setting
∆Pv = Pressure loss across valve

## Frese PV Compact
QUICK - CALC Frese PV Compact
Setting & Selection program PV Compact Differential Pressure Control Valve
Input
Input ∆Ps = |  | 20 | (kPa) Differential Pessure setting
Input Q = |  | 1000 | (l/h) Design flow
Dim. | ∆Ps range | Range |  | Pre-set
|  | Flow (l/h) | Range ∆Pp (kPa) | Number of turns
DN15 | 5-30 kPa | 50-600 | 5-450 | NOT POSSIBLE
DN15 | 20-60 kPa | 100-1000 | 20-450 | 2.9
DN20 | 5-30 kPa | 100-1000 | 5-450 | 13.6765
DN20 | 20-60 kPa | 150-2000 | 20-450 | 2.8949
DN25 | 5-30 kPa | 600-2100 | 5-450 | 10.3856
DN25 | 20-80 kPa | 750-4200 | 20-450 | 0.19746
DN32 | 20-80 kPa | 1000-5000 | 20-450 | -0.037361
DN40 | 20-80 kPa | 3000-8000 | 20-450 | NOT POSSIBLE
DN50 | 20-80 kPa | 5000-11500 | 20-450 | NOT POSSIBLE
Calculation of pressure loss
Dimension |  | ∆Pv (kPa) | Min. ∆Pp (kPa)
DN15 5-30 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN15 20-60 kPa |  | 11.8906 | 31.8906
DN20 5-30 kPa |  | 8.1633 | 28.1633
DN20 20-60 kPa |  | 8.1633 | 28.1633
DN25 5-30 kPa |  | 6.25 | 26.25
DN25 20-80 kPa |  | 1.3212 | 21.3212
DN32 20-80 kPa |  | 0.9803 | 20.9803
DN40 20-80 kPa |  | NOT POSSIBLE | NOT POSSIBLE
DN50 20-80 kPa |  | NOT POSSIBLE | NOT POSSIBLE
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN
Type |  | X | Y | Z | Kvs | Min | Max | Evaluering af Flow | Evaluering af Dp
DN15 5-30 kPa |  | 5 | 272 | 0.68 | 2.9 | 50 | 600 | UDEN FOR OMRÅDET | 20
DN15 20-60 kPa |  | 20 | 312.5 | 0.4015 | 2.9 | 100 | 1000 | 1000 | 20
DN20 5-30 kPa |  | 5 | 272 | 0.68 | 3.5 | 100 | 1000 | 1000 | 20
DN20 20-60 kPa |  | 20 | 313 | 0.402 | 3.5 | 150 | 2000 | 1000 | 20
DN25 5-30 kPa |  | 5 | 322 | 0.612 | 4 | 600 | 2100 | 1000 | 20
DN25 20-80 kPa |  | 20 | 1180 | 0.285 | 8.7 | 750 | 4200 | 1000 | 20
DN32 20-80 kPa |  | 20 | 1201 | 0.275 | 10.1 | 1000 | 5000 | 1000 | 20
DN40 20-80 kPa |  | 20 | 2411 | 0.299 | 15.8 | 3000 | 8000 | UDEN FOR OMRÅDET | 20
DN50 20-80 kPa |  | 20 | 1547 | 0.23 | 16.2 | 5000 | 11500 | UDEN FOR OMRÅDET | 20
∆Pp = Pump pressure
∆Ps = Differential pressure setting
∆Pv = Pressure loss across valve

## Frese PVS
QUICK - CALC Frese PVS | [9 empty] | QUICK - CALC Frese S
Selection program Frese PVS Differential Pressure & Dynamic Flow Control | [9 empty] | Auslegungsprogramm für Frese S Dynamischer Volumenstromregler
| Input | [9 empty] | Eingabe
Input ∆Ps = | 10 | (kPa) Differential pressure setting | [7 empty] | Eingabe dP = | 20 | (kPa) Differenzdruck am Ventil
Input Q = | 1200 | (l/h) Design flow in Zone | [7 empty] | Eingabe Q = | 25 | (l/h) Auslegungsvolumenstrom | (L/h) Auslegungsvolumenstrom
Frese PV (Return) |  | Frese S (Supply) |  |  |  | PVS System
Pre-set Frese PV |  | Pre-set Frese S |  |  |  | Total Pressure loss
Dimension | Number of turns | Dimension | Pre-set | Kv | Min. ∆P (kPa) | Min. ∆Pp (kPa)
DN15 5-30 kPa | NOT POSSIBLE | DN15 LP | NOT POSSIBLE | #VALUE! | NICHT MÖGLICH | NOT POSSIBLE
DN15 20-60 kPa | NOT POSSIBLE | DN15 HP | NOT POSSIBLE | #VALUE! | NICHT MÖGLICH | NOT POSSIBLE
DN20 5-30kPa | NOT POSSIBLE | DN20 LP | 9.0101 | 3.1677 | 14.3508 | NOT POSSIBLE
DN20 20-60kPa | NOT POSSIBLE | DN20 HP | 6.7839 | 2.6336 | 20.7622 | NOT POSSIBLE
DN25 5-30 kPa | 8.995 | DN25 LP | 6.4402 | 3.1622 | 14.4003 | 25.9959
DN25 20-60 kPa | NOT POSSIBLE | DN25 HP | 4.8698 | 2.7192 | 19.4744 | NOT POSSIBLE
DN32 20-80 kPa | NOT POSSIBLE | DN32 HP | 2.9228 | 2.8834 | 17.3203 | NOT POSSIBLE
DN40 20-80 kPa | NOT POSSIBLE | DN40 HP | 2.4488 | 2.9042 | 17.0726 | NOT POSSIBLE
DN50 20-80 kPa | NOT POSSIBLE | DN50 HP | 1.6696 | 2.809 | 18.2498 | NOT POSSIBLE
∆Pv (kPa)
NOT POSSIBLE
NOT POSSIBLE
1.5956
NOT POSSIBLE
NOT POSSIBLE
NOT POSSIBLE
2
Dim. ∆Ps Rang. | Frese PV ∆P - Controller |  | Frese S Flow Controller |  |  |  | Frese PV&S ∆P & Flow Controller
| Flow range (l/h) | ∆Pp range (kPa) | Flow range (l/h) |  |  | ∆Pp range (kPa) | ∆Ps range (kPa) | Flow range (l/h) | ∆Pp range (kPa)
DN15 5-30kPa | 50-600 | 5-400 | 25-804 |  |  | 8-250 | 5-30 | 50-600 | 14-250
DN15 20-60kPa | 100-1200 | 20-400 | 40-1100 |  |  | 16-400 | 20-60 | 100-1100 | 37-400
DN20 5-30 kPa | 100-1000 | 5-400 | 41-1265 |  |  | 9-250 | 5-30 | 100-1000 | 14-250
DN20 20-60kPa | 150-2000 | 20-400 | 66-1850 |  |  | 12-400 | 20-60 | 150-1850 | 33-400
DN25 5-30kPa | 600-2500 | 5-400 | 61-1663 |  |  | 9-250 | 5-30 | 600-1663 | 17-250
DN25 20-60kPa | 700-4000 | 20-400 | 89-2350 |  |  | 12-400 | 20-60 | 700-2350 | 37-400
DN32 20-80kPa | 1000-5000 | 20-400 | 217-4800 |  |  | 14-400 | 20-80 | 1000-4800 | 38-400
DN40 20-80kPa | 3000-8000 | 20-400 | 175-7450 |  |  | 15-400 | 20-80 | 3000-7450 | 45-400
DN50 20-80kPa | 5000-15000 | 20-400 | 440-10350 |  |  | 17-400 | 20-80 | 5000-10350 | 57-400 | Der Regelbereich ist definiert von Min. Pumpendruck (Min. ∆Pp) bis Max. Pumpendruck (Max.∆Pp) .
ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN | [9 empty] | ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN
Type | X | Y | Z | Kvs | Min | Max |  | Evaluering af Flow | Evaluering af Dp | Type | X | Y | Z | Kvs | Min | Max | Evaluering af Flow | Evaluering af Dp
DN15 5-30 kPa | 5 | 494.76 | 0.5575 | 3.6 | 50 | 600 |  | UDEN FOR OMRÅDET | 10 | DN15 LP |  |  |  | 2.2 | 25 | 804 | UDEN FOR OMRÅDET | 20
DN15 20-60 kPa | 20 | 747.59 | 0.3133 | 3.6 | 100 | 1200 |  | 1200 | UDEN FOR OMRÅDET | DN15 HP |  |  |  | 2.4 | 40 | 1100 | UDEN FOR OMRÅDET | 20
DN20 5-30 kPa | 5 | 682.82 | 0.59 | 4 | 100 | 1000 |  | UDEN FOR OMRÅDET | 10 | DN20 LP |  |  |  | 3.3 | 41 | 1265 | 1200 | 20
DN20 20-60 kPa | 20 | 596.44 | 0.324 | 4 | 150 | 2000 |  | 1200 | UDEN FOR OMRÅDET | DN20 HP |  |  |  | 3.6 | 66 | 1850 | 1200 | 20
DN25 5-30 kPa | 5 | 802.65 | 1.26 | 9.5 | 600 | 2500 |  | 1200 | 10 | DN25 LP |  |  |  | 4.1 | 61 | 1663 | 1200 | 20
DN25 20-60 kPa | 20 | 1529.6 | 0.7175 | 9.5 | 700 | 4200 |  | 1200 | UDEN FOR OMRÅDET | DN25 HP |  |  |  | 4.4 | 89 | 2350 | 1200 | 20
DN32 20-80 kPa | 20 | 1338.84 | 0.4833 | 11.4 | 1000 | 4800 |  | 1200 | UDEN FOR OMRÅDET | DN32 |  |  |  | 8.8 | 217 | 4800 | 1200 | 20
DN40 20-80 kPa | 20 | 2213.08 | 0.4133 | 16.4 | 3000 | 7450 |  | UDEN FOR OMRÅDET | UDEN FOR OMRÅDET | DN40 |  |  |  | 13.2 | 175 | 7450 | 1200 | 20
DN50 20-80 kPa | 20 | 2234.42 | 0.352 | 17.9 | 5000 | 10350 |  | UDEN FOR OMRÅDET | UDEN FOR OMRÅDET | DN50 |  |  |  | 16.7 | 440 | 10350 | 1200 | 20
∆Pp = Pump pressure
∆Ps = Differential pressure setting
∆Pv = Pressure loss across valve
S
PV
Frese S (Supply)
Frese PV (Return)
Frese PV
Frese S

## Frese PV-SIGMA
QUICK - CALC Frese PV-SIGMA Compact | [9 empty] | QUICK - CALC Frese S
Selection program Frese PV-SIGMA Compact Differential Pressure & Dynamic Flow Control | [9 empty] | Auslegungsprogramm für Frese S Dynamischer Volumenstromregler
| Input | [9 empty] | Eingabe
Input ∆Ps = | 30 | (kPa) Differential pressure in system | [7 empty] | Eingabe dP = | 20 | (kPa) Differenzdruck am Ventil
Input Q = | 500 | (l/h) Design flow in system | [7 empty] | Eingabe Q = | 25 | (l/h) Auslegungsvolumenstrom | (L/h) Auslegungsvolumenstrom
PV Compact (Return) |  | SIGMA Compact (Supply) |  |  |  | PV-SIGMA System
Pre-set PV Compact |  | Pre-set SIGMA Compact |  |  |  | Total pressure loss
Dimension | Number of turns | Dimension | Pre-set |  | Min. ∆P (kPa) | Min. ∆Pp (kPa)
DN15 5-30 kPa | 18.6382 | DN15 Low | 2.2088 |  | 11.1 | 44.0727
DN15 20-60 kPa | 5.315 | DN15 High | 1.9 |  | 14.3 | 47.2727
DN20 5-30kPa | 18.6382 | DN20 Low | 1.1286 |  | 9 | 41.0408
DN20 20-60kPa | 5.3174 | DN20 High | 0.9 |  | 16 | 48.0408
DN25 5-30 kPa | NOT POSSIBLE | DN25 High | 0.9 |  | 14 | NOT POSSIBLE
DN25 20-80 kPa | NOT POSSIBLE | DN25 High | 0.9 |  | 14 | NOT POSSIBLE
DN32 20-80 kPa | NOT POSSIBLE | DN32 | 0.70002 |  | 15 | NOT POSSIBLE
DN40 20-80 kPa | NOT POSSIBLE | DN40 | NOT POSSIBLE |  | #VALUE! | NOT POSSIBLE
DN50 20-80 kPa | NOT POSSIBLE | DN50 | NOT POSSIBLE |  | #VALUE! | NOT POSSIBLE
∆P-PV (kPa)
2.9727
2.9727
2.0408
2.0408
NOT POSSIBLE
NOT POSSIBLE
NOT POSSIBLE
NOT POSSIBLE
NOT POSSIBLE
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
| PV Compact ∆P - Controller |  | SIGMA Compact Flow Controller |  |  |  | PV-SIGMA Compact System ∆P & Flow controller
Dim. ∆Ps Range | Flow range (l/h) | ∆Pp range (kPa) | Flow range (l/h) |  |  | ∆Pp range (kPa) | ∆Ps range (kPa) | Flow range (l/h) | ∆Pp range (kPa)
DN15 5-30kPa | 50-600 | 7-450 | 40-900 |  |  | 10-400 | 5-30 | 50-600 | 10-400
DN15 20-60kPa | 100-1000 | 22-450 | 60-1080 |  |  | 14-400 | 20-60 | 100-1000 | 22-400
DN20 5-30 kPa | 100-1000 | 7-450 | 86-1550 |  |  | 9-400 | 5-30 | 100-1000 | 9-400
DN20 20-60 kPa | 150-2000 | 22-450 | 102-1930 |  |  | 16-400 | 20-60 | 150-1930 | 22-400
DN25 5-30kPa | 600-2100 | 7-450 | 137-2400 |  |  | 14-400 | 5-30 | 600-2100 | 14-400
DN25 20-80kPa | 750-4200 | 22-450 | 137-2400 |  |  | 14-400 | 20-80 | 750-2400 | 22-400
DN32 20-80kPa | 1000-5000 | 22-450 | 200-5000 |  |  | 15-400 | 20-80 | 1000-5000 | 22-400
DN40 20-80kPa | 3000-8000 | 22-450 | 719-7400 |  |  | 10-400 | 20-80 | 3000-7400 | 22-400
DN50 20-80kPa | 5000-11500 | 22-450 | 900-10350 |  |  | 10-400 | 20-80 | 5000-10350 | 22-400 | Der Regelbereich ist definiert von Min. Pumpendruck (Min. ∆Pp) bis Max. Pumpendruck (Max.∆Pp) .
ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN | [9 empty] | ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN
Type |  | X (min Kpa) | Y (Flow/Omdr) | Z (Omdr/kpa) | Kvs | Min | Max | Evaluering af Flow | Evaluering af Dp | Type | X | Y | Z | Kvs | Min | Max | Evaluering af Flow | Evaluering af Dp
DN15 5-30 kPa |  | 5 | 272 | 0.68 | 2.9 | 50 | 600 | 500 | 30 | DN15 LF |  |  |  | 2.6 | 40 | 900 | 500 | 30
DN15 20-60 kPa |  | 20 | 312.5 | 0.4015 | 2.9 | 100 | 1000 | 500 | 30 | DN15 HF |  |  |  | 2.6 | 60 | 1080 | 500 | 30
DN20 5-30 kPa |  | 5 | 272 | 0.68 | 3.5 | 100 | 1000 | 500 | 30 | DN20 LF |  |  |  | 4 | 86 | 1550 | 500 | 30
DN20 20-60 kPa |  | 20 | 313 | 0.402 | 3.5 | 150 | 2000 | 500 | 30 | DN20 HF |  |  |  | 4 | 102 | 1930 | 500 | 30
DN25 5-30 kPa |  | 5 | 321.5 | 0.612 | 4 | 600 | 2100 | UDEN FOR OMRÅDET | 30 | DN25 HF |  |  |  | 4.2 | 137 | 2400 | 500 | 30
DN25 20-80 kPa |  | 20 | 1180 | 0.285 | 8.7 | 750 | 4200 | UDEN FOR OMRÅDET | 30 | DN25 HF |  |  |  | 4.2 | 137 | 2400 | 500 | 30
DN32 20-80 kPa |  | 20 | 1201 | 0.275 | 10.1 | 1000 | 5000 | UDEN FOR OMRÅDET | 30 | DN32 |  |  |  | 10.9 | 200 | 5000 | 500 | 30
DN40 20-80 kPa |  | 20 | 2410.7 | 0.2988 | 15.8 | 3000 | 8000 | UDEN FOR OMRÅDET | 30 | DN40 |  |  |  | 18 | 719 | 7400 | UDEN FOR OMRÅDET | 30
DN50 20-80 kPa |  | 20 | 1547 | 0.23 | 16.2 | 5000 | 11500 | UDEN FOR OMRÅDET | 30 | DN50 |  |  |  | 20.3 | 900 | 10350 | UDEN FOR OMRÅDET | 30
∆Pp = Pump pressure
∆Ps = Differential pressure in system
∆Pv = Pressure loss across valve
Frese SIGMA Compact (Supply)
Frese PV Compact (Return)
Frese PV Compact
Frese SIGMA Compact
∆Pv
∆Pv
∆Ps
∆Pp
∆Pp = ∆Ps + ∆Pv

## ALPHA
Quick - CALC Frese ALPHA
Selection program Frese ALPHA Dynamic Balancing Valve
|  |  | Input |  | CARTRIDGE SELECTION |  |  |  | Flow | Min. ΔP | Item no. | Item no. | Deviation
| Input Q = |  | 1000 | (l/h) Flow | with selected Valve dimension (DN) |  |  |  | l/h | kPa | LP | HP
| ΔP range (kPa) | DN15-25 | DN25L-50 |  | Nearest higher Flow |  |  |  | 1020 | 12 | 50-33089 | 49-33089 | 2%
| LP Low Press. | 7-350 | 12-350
| HP High Press. | 7-600 | 12-600 |  | Nearest lower Flow |  |  |  | 861 | 12 | 50-33082 | 49-33082 | -13.9%
[7 empty] | Plugs |  | Drain Valve |  | P/T-Plugs
| Dimension Valve house DN | [5 empty] | ALPHA | Item no. | ALPHA | Item no. | ALPHA | Item no.
| Input DN = |  | 50 |  |  |  | 50 | 49-9066 | 50 | 49-9064 | 50 | 49-9061
ALPHA Valve
| Valve | Flow
| Dimension | range
| DN | l/h
| 15 | 25-2448
| 20 | 25-2448
| 25 | 25-2448
| 25L | 674-11355
| 32 | 674-11355
| 40 | 674-11355
| 50 | 674-11355
| Alpha Regler |  | Berechnung nächst kleiner Volumenstrom |  |  |  | Berechnung nächst größer Volumenstrom |  |  |  | Alpha Ventilgehäuse Modell
| Ventil | Vol.- | Vol.- | Min. ΔP | Art.-Nr. | Art.-Nr. | Vol.- | Min. ΔP | Art.-Nr. | Art.-Nr. | Art.-Nr. | Art.-Nr. | Art.-Nr.
| Dimension | Bereich | Strom |  | LP-Einsatz | HP-Einsatz | Strom |  | LP-Einsatz | HP-Einsatz | Alpha S | Alpha FE | Alpha DM
| DN | L/h | L/h | kPa | bis 3,5 bar | bis 6,0 bar | L/h | kPa | bis 3,5 bar | bis 6,0 bar | IG/IG | IG/IG | IG/IG
| 15 | 25-2448 | 936 | 21 | 50-11750 | 49-11750 | 1020 | 22 | 50-20700 | 49-20700 | 49-9006 | 49-9004 | 49-9001
| 20 | 25-2448 | 936 | 21 | 50-11750 | 49-11750 | 1020 | 22 | 50-20700 | 49-20700 | 49-9016 | 49-9014 | 49-9011
| 25 | 25-2448 | 936 | 21 | 50-11750 | 49-11750 | 1020 | 22 | 50-20700 | 49-20700 | 49-9026 | 49-9024 | 49-9021
| 25L | 674-11355 | 861 | 12 | 50-33082 | 49-33082 | 1020 | 12 | 50-33089 | 49-33089 | 49-9036 | 49-9034 | 49-9031
| 32 | 674-11355 | 861 | 12 | 50-33082 | 49-33082 | 1020 | 12 | 50-33089 | 49-33089 | 49-9046 | 49-9044 | 49-9041
| 40 | 674-11355 | 861 | 12 | 50-33082 | 49-33082 | 1020 | 12 | 50-33089 | 49-33089 | 49-9056 | 49-9054 | 49-9051
| 50 | 674-11355 | 861 | 12 | 50-33082 | 49-33082 | 1020 | 12 | 50-33089 | 49-33089 | 49-9066 | 49-9064 | 49-9061
| DN15-DN25 | [7 empty] | DN25L-DN50 | [7 empty] | Gehäuse sind mit Stopfen, Druckmessnippel oder Füll- und Entleerungskugelhahn
| Kleiner |  |  |  | Grosser |  |  |  | Kleiner |  |  |  | Grosser
| L/h | Min | Vare nr. |  | L/h | Min | Vare nr. |  | L/h | Min | Vare nr. |  | L/h | Min | Vare nr. |  | Der Regelbereich = S ….
|  | DP | LP | HP |  | DP | LP | HP |  | DP | LP | HP |  | DP | LP | HP
| 0 |  |  |  | 25 | 7 | 50-11150 | N/A | 0 |  |  |  | 674 | 12 | 50-33073 | 49-33073
| 25 | 7 | 50-11150 | N/A | 36 | 7 | 50-11170 | N/A | 674 | 12 | 50-33073 | 49-33073 | 861 | 12 | 50-33082 | 49-33082
| 36 | 7 | 50-11170 | N/A | 43 | 7 | 50-11190 | N/A | 861 | 12 | 50-33082 | 49-33082 | 1020 | 12 | 50-33089 | 49-33089
| 43 | 7 | 50-11190 | N/A | 55 | 7 | 50-11210 | 49-11210 | 1020 | 12 | 50-33089 | 49-33089 | 1136 | 12 | 50-33094 | 49-33094
| 55 | 7 | 50-11210 | 49-11210 | 75 | 8 | 50-11230 | 49-11230 | 1136 | 12 | 50-33094 | 49-33094 | 1190 | 12 | 50-33096 | 49-33096
| 75 | 8 | 50-11230 | 49-11230 | 84 | 9 | 50-11260 | 49-11260 | 1190 | 12 | 50-33096 | 49-33096 | 1272 | 13 | 50-33098 | 49-33098
| 84 | 9 | 50-11260 | 49-11260 | 104 | 10 | 50-11290 | 49-11290 | 1272 | 13 | 50-33098 | 49-33098 | 1349 | 13 | 50-33102 | 49-33102
| 104 | 10 | 50-11290 | 49-11290 | 114 | 10 | 50-11300 | 49-11300 | 1349 | 13 | 50-33102 | 49-33102 | 1485 | 13 | 50-33107 | 49-33107
| 114 | 10 | 50-11300 | 49-11300 | 129 | 11 | 50-11320 | 49-11320 | 1485 | 13 | 50-33107 | 49-33107 | 1567 | 14 | 50-33111 | 49-33111
| 129 | 11 | 50-11320 | 49-11320 | 154 | 11 | 50-11350 | 49-11350 | 1567 | 14 | 50-33111 | 49-33111 | 1631 | 14 | 50-33112 | 49-33112
| 154 | 11 | 50-11350 | 49-11350 | 175 | 12 | 50-11370 | 49-11370 | 1631 | 14 | 50-33112 | 49-33112 | 1815 | 14 | 50-33118 | 49-33118
| 175 | 12 | 50-11370 | 49-11370 | 204 | 12 | 50-11400 | 49-11400 | 1815 | 14 | 50-33118 | 49-33118 | 2001 | 15 | 50-33124 | 49-33124
| 204 | 12 | 50-11400 | 49-11400 | 241 | 12 | 50-11430 | 49-11430 | 2001 | 15 | 50-33124 | 49-33124 | 2044 | 16 | 50-33125 | 49-33125
| 241 | 12 | 50-11430 | 49-11430 | 279 | 12 | 50-11460 | 49-11460 | 2044 | 16 | 50-33125 | 49-33125 | 2171 | 16 | 50-33129 | 49-33129
| 279 | 12 | 50-11460 | 49-11460 | 320 | 13 | 50-11490 | 49-11490 | 2171 | 16 | 50-33129 | 49-33129 | 2271 | 17 | 50-33132 | 49-33132
| 320 | 13 | 50-11490 | 49-11490 | 350 | 13 | 50-11510 | 49-11510 | 2271 | 17 | 50-33132 | 49-33132 | 2380 | 17 | 50-33135 | 49-33135
| 350 | 13 | 50-11510 | 49-11510 | 400 | 13 | 50-11540 | 49-11540 | 2380 | 17 | 50-33135 | 49-33135 | 2498 | 18 | 50-33138 | 49-33138
| 400 | 13 | 50-11540 | 49-11540 | 477 | 14 | 50-11570 | 49-11570 | 2498 | 18 | 50-33138 | 49-33138 | 2639 | 18 | 50-33142 | 49-33142
| 477 | 14 | 50-11570 | 49-11570 | 545 | 14 | 50-11620 | 49-11620 | 2639 | 18 | 50-33142 | 49-33142 | 2871 | 19 | 50-33148 | 49-33148
| 545 | 14 | 50-11620 | 49-11620 | 615 | 14 | 50-11725 | 49-11725 | 2871 | 19 | 50-33148 | 49-33148 | 3191 | 21 | 50-33156 | 49-33156
| 615 | 14 | 50-11725 | 49-11725 | 670 | 14 | 50-11730 | 49-11730 | 3191 | 21 | 50-33156 | 49-33156 | 3407 | 22 | 50-33161 | 49-33161
| 670 | 14 | 50-11730 | 49-11730 | 736 | 14 | 50-11735 | 49-11735 | 3407 | 22 | 50-33161 | 49-33161 | 3486 | 22 | 50-33163 | 49-33163
| 736 | 14 | 50-11735 | 49-11735 | 799 | 16 | 50-11740 | 49-11740 | 3486 | 22 | 50-33163 | 49-33163 | 3634 | 20 | 50-44148 | 49-44148
| 799 | 16 | 50-11740 | 49-11740 | 870 | 19 | 50-11745 | 49-11745 | 3634 | 20 | 50-44148 | 49-44148 | 3681 | 21 | 50-44152 | 49-44152
| 870 | 19 | 50-11745 | 49-11745 | 936 | 21 | 50-11750 | 49-11750 | 3681 | 21 | 50-44152 | 49-44152 | 4088 | 21 | 50-44156 | 49-44156
| 936 | 21 | 50-11750 | 49-11750 | 1020 | 22 | 50-20700 | 49-20700 | 4088 | 21 | 50-44156 | 49-44156 | 4315 | 21 | 50-44164 | 49-44164
| 1020 | 22 | 50-20700 | 49-20700 | 1081 | 22 | 50-20740 | 49-20740 | 4315 | 21 | 50-44164 | 49-44164 | 4542 | 22 | 50-44168 | 49-44168
| 1081 | 22 | 50-20740 | 49-20740 | 1195 | 22 | 50-20770 | 49-20770 | 4542 | 22 | 50-44168 | 49-44168 | 4769 | 22 | 50-44173 | 49-44173
| 1195 | 22 | 50-20770 | 49-20770 | 1335 | 23 | 50-20820 | 49-20820 | 4769 | 22 | 50-44173 | 49-44173 | 4996 | 23 | 50-44176 | 49-44176
| 1335 | 23 | 50-20820 | 49-20820 | 1483 | 23 | 50-20860 | 49-20860 | 4996 | 23 | 50-44176 | 49-44176 | 5450 | 24 | 50-44182 | 49-44182
| 1483 | 23 | 50-20860 | 49-20860 | 1581 | 23 | 50-20880 | 49-20880 | 5450 | 24 | 50-44182 | 49-44182 | 5905 | 25 | 50-44191 | 49-44191
| 1581 | 23 | 50-20880 | 49-20880 | 1774 | 24 | 50-20920 | 49-20920 | 5905 | 25 | 50-44191 | 49-44191 | 6539 | 26 | 50-44194 | 49-44194
| 1774 | 24 | 50-20920 | 49-20920 | 1883 | 24 | 50-20940 | 49-20940 | 6539 | 26 | 50-44194 | 49-44194 | 6831 | 27 | 50-44200 | 49-44200
| 1883 | 24 | 50-20940 | 49-20940 | 2080 | 25 | 50-20990 | 49-20990 | 6831 | 27 | 50-44200 | 49-44200 | 7267 | 28 | 50-44205 | 49-44205
| 2080 | 25 | 50-20990 | 49-20990 | 2251 | 26 | 50-21030 | 49-21030 | 7267 | 28 | 50-44205 | 49-44205 | 7721 | 30 | 50-44211 | 49-44211
| 2251 | 26 | 50-21030 | 49-21030 | 2319 | 27 | 50-21060 | 49-21060 | 7721 | 30 | 50-44211 | 49-44211 | 8176 | 31 | 50-44217 | 49-44217
| 2319 | 27 | 50-21060 | 49-21060 | 2448 | 28 | 50-21090 | 49-21090 | 8176 | 31 | 50-44217 | 49-44217 | 8630 | 33 | 50-44222 | 49-44222
| 2448 | 28 | 50-21090 | 49-21090 | 2448 | 28 | 50-21090 | 49-21090 | 8630 | 33 | 50-44222 | 49-44222 | 9084 | 34 | 50-44229 | 49-44229
[9 empty] | 9084 | 34 | 50-44229 | 49-44229 | 9538 | 36 | 50-44235 | 49-44235
[9 empty] | 9538 | 36 | 50-44235 | 49-44235 | 9990 | 38 | 50-44241 | 49-44241
[9 empty] | 9990 | 38 | 50-44241 | 49-44241 | 10445 | 40 | 50-44248 | 49-44248
[9 empty] | 10445 | 40 | 50-44248 | 49-44248 | 10900 | 42 | 50-44250 | 49-44250
[9 empty] | 10900 | 42 | 50-44250 | 49-44250 | 11355 | 44 | 50-44262 | 49-44262
[9 empty] | 11355 | 44 | 50-44262 | 49-44262 | 11355 | 44 | 50-44262 | 49-44262

## ALPHA Wafer
QUICK - CALC Frese ALPHA Flange
Selection program Frese ALPHA Wafer Dynamic Balancing Valve
|  |  | Input |  | CARTRIDGE SELECTION |  |  | Flow | Min. ΔP | Qty | Vare nr. | Flow |  | Qty | Item no. | Flow | Deviation
| Input Q = |  | 175.32 | m³/h Flow | with selected Valve dimension (DN) |  |  | m³/h | kPa | Cartriges |  |  |  | Cartridges
[5 empty] | Nearest higher Flow |  |  | 175.5 | 23 | 13 | 52-55292 | 12.5 |  | 2 | 52-55243 | 6.5 | 0.1027%
Cartridge Type HP (High Pressure)
| AISI 304 |  |  |  | Nearest lower Flow |  |  | 171 | 22 | 15 | 52-55287 | 11.4 |  |  |  |  | -2.464%
ΔP range: 13 - 600 kPa
Dimension Valve house DN
| Input DN = |  | 300
| Item no. Valve house |  | 49-9143-01
|  |  | Berechnungen Nächst kleiner Volumenstrom : |  |  |  |  | Berechnungen Nächst größer Volumenstrom :
Ventil | Vol.-Ber. | Anzahl | Vol.-Str | Min ΔP | Art.-Nr. | Vol.-Strom | Ist/Soll | Vol.-Strom | Min. ΔP | Anzahl | Art.-Nr. | Vol.- | Anz | Rest | Art.-Nr. | Vol.- | Ist/Soll
Dim. | m³/h | Einsätze | m³/h | kPa |  | m³/h | Abw. | m³/h | kPa | Einsätze |  | Strom | Eins | Vol.-Str |  | Strom | Abw.
DN |  |  | Regler Komplett |  | Einsatz | Einsatz |  | Regler Komplett |  |  | Einsatz | Eins. |  | m³/h | Einsatz | Eins.
50 | 3,8 - 45,0 | 1 | 45 | 49 | 52-66407H | 45 | -74.33% | 45 | 49 | 1 | 52-66407H | 45 | 0 | 130.32 | 0 | 0 | -74.33%
65 | 3,8 - 45,0 | 1 | 45 | 49 | 52-66407H | 45 | -74.33% | 45 | 49 | 1 | 52-66407H | 45 | 0 | 130.32 | 0 | 0 | -74.33%
80 | 3,8 - 45,0 | 1 | 45 | 49 | 52-66407H | 45 | -74.33% | 45 | 49 | 1 | 52-66407H | 45 | 0 | 130.32 | 0 | 0 | -74.33%
100 | 3,8 - 90,0 | 2 | 90 | 49 | 52-66407H | 45 | -48.67% | 90 | 49 | 1 | 52-66407H | 45 | 1 | 130.32 | 52-66407H | 45 | -48.67%
125 | 3,8 - 135,0 | 3 | 135 | 49 | 52-66407H | 45 | -23% | 135 | 49 | 2 | 52-66407H | 45 | 1 | 85.32 | 52-66407H | 45 | -23%
150 | 3,8 - 180,0 | 4 | 164 | 46 | 52-66407 | 41 | -6.457% | 176 | 49 | 3 | 52-66407H | 45 | 1 | 40.32 | 52-66407 | 41 | 0.3879%
200 | 3,8 - 315,0 | 7 | 171.5 | 37 | 52-66338 | 24.5 | -2.179% | 176 | 38 | 6 | 52-66344 | 25.6 | 1 | 21.72 | 52-66326 | 22.4 | 0.3879%
250 | 3,8 - 540,0 | 12 | 160.8 | 24 | 52-55298 | 13.4 | -8.282% | 177.6 | 27 | 10 | 52-55303 | 14.8 | 2 | 13.66 | 52-55303 | 14.8 | 1.3%
300 | 3,8 - 675,0 | 15 | 171 | 22 | 52-55287 | 11.4 | -2.464% | 175.5 | 23 | 13 | 52-55292 | 12.5 | 2 | 6.41 | 52-55243 | 6.5 | 0.1027%
350 | 3,8 - 855,0 | 19 | 169.1 | 16 | 52-55269 | 8.9 | -3.548% | 177.8 | 19 | 16 | 52-55279 | 10.4 | 3 | 2.9733 | 52-55179 | 3.8 | 1.415%
400 | 3,8 - 1.170,0 | 26 | 169 | 14 | 52-55243 | 6.5 | -3.605% | 175.6 | 14 | 21 | 52-55251 | 7.1 | 5 | 5.244 | 52-55220 | 5.3 | 0.1597%
450 | 3,8 - 1.485,0 | 33 | 174.9 | 14 | 52-55220 | 5.3 | -0.2396% | 177.1 | 14 | 23 | 52-55227 | 5.7 | 10 | 4.422 | 52-55206 | 4.6 | 1.015%
500 | 3,8 - 1.800,0 | 40 | 168 | 13 | 52-55194 | 4.2 | -4.175% | 176 | 13 | 30 | 52-55200 | 4.4 | 10 | 4.332 | 52-55200 | 4.4 | 0.3879%
600 | 3,8 - 2.520,0 | 56 | 168 | 13 | 52-55194 | 4.2 | -4.175% | 176 | 13 | 30 | 52-55200 | 4.4 | 10 | 4.332 | 52-55200 | 4.4 | 0.3879%
800 | 3,8 - 3.825,0 | 85 | 168 | 13 | 52-55194 | 4.2 | -4.175% | 176 | 13 | 30 | 52-55200 | 4.4 | 10 | 4.332 | 52-55200 | 4.4 | 0.3879%
| '=((SVERWEIS(($D$5/$C17);$D$40:$F$84;1)*C17)) | [6 empty] | Flow > | =((SVERWEIS(($D$5/$C22);$C$38:$I$81;1)*(C22-1)))
| '=WENN($D$5/$C23<3,8;SVERWEIS(($D$5/$C22);$D$40:$F$84;1);SVERWEIS(($D$5/$C23);$D$40:$F$84;1)) | [10 empty] | Korrektion til slut :
| '=WENN($D$5/$C24<3,8;D23;SVERWEIS(($D$5/$C24);$D$40:$F$84;1)) | [10 empty] | Spalte D:H Min el slettes
DN50-DN800
|  | Kleiner |  |  |  | Grosser | [5 empty] | WENN(Prüfung;Dann_Wert; WENN(Prüfung;Dann_Wert;Sonst_Wert))
|  | L/h | m³/h | Min |  | m³/h | Min
|  |  |  | DP | Vare nr. |  | DP | Vare nr. |  |  |  | SVERWEIS(Suchkriterium;Matrix;Spalteindex;Bereich_Verweis)
0
|  |  | 0 |  |  | 3.8 | 13 | 52-55179 |  | 45 | D | '=((SVERWEIS(($D$5/$C17);$D$40:$F$84;1)*C17))
|  | 3820 | 3.8 | 13 | 52-55179 | 3.9 | 13 | 52-55184 |  | 49 | E | '=SVERWEIS(($D$5/$C17);$D$40:$F$84;2)
|  | 3931 | 3.9 | 13 | 52-55184 | 4 | 13 | 52-55189 |  | 52-66407H | F | '=SVERWEIS(($D$5/$C17);$D$40:$F$84;3)
|  | 4049 | 4 | 13 | 52-55189 | 4.2 | 13 | 52-55194 |  | 45 | G | '=SVERWEIS(($D$5/$C17);$D$40:$F$84;1)
|  | 4199 | 4.2 | 13 | 52-55194 | 4.4 | 13 | 52-55200
|  | 4399 | 4.4 | 13 | 52-55200 | 4.6 | 14 | 52-55206
|  | 4640 | 4.6 | 14 | 52-55206 | 5 | 14 | 52-55213 |  | WENN(O23<0;
|  | 4951 | 5 | 14 | 52-55213 | 5.3 | 14 | 52-55220
|  | 5310 | 5.3 | 14 | 52-55220 | 5.7 | 14 | 52-55227
|  | 5700 | 5.7 | 14 | 52-55227 | 6.2 | 14 | 52-55235 |  | DN | Art.-Nr. Gehäuse
|  | 6209 | 6.2 | 14 | 52-55235 | 6.5 | 14 | 52-55243 |  | 50 | 49-9073-01
|  | 6511 | 6.5 | 14 | 52-55243 | 7.1 | 14 | 52-55251 |  | 65 | 49-9083-01
|  | 7081 | 7.1 | 14 | 52-55251 | 7.9 | 15 | 52-55260 |  | 80 | 49-9093-01
|  | 7901 | 7.9 | 15 | 52-55260 | 8.9 | 16 | 52-55269 |  | 100 | 49-9103-01
|  | 8900 | 8.9 | 16 | 52-55269 | 10.4 | 19 | 52-55279 |  | 125 | 49-9163-01
|  | 10399 | 10.4 | 19 | 52-55279 | 11.4 | 22 | 52-55287 |  | 150 | 49-9113-01
|  | 11355 | 11.4 | 22 | 52-55287 | 12.5 | 23 | 52-55292 |  | 200 | 49-9123-01
|  | 12491 | 12.5 | 23 | 52-55292 | 13.4 | 24 | 52-55298 |  | 250 | 49-9133-01
|  | 13399 | 13.4 | 24 | 52-55298 | 14.8 | 27 | 52-55303 |  | 300 | 49-9143-01
|  | 14762 | 14.8 | 27 | 52-55303 | 16 | 29 | 52-55308 |  | 350 | 49-9153-01
|  | 15999 | 16 | 29 | 52-55308 | 17 | 34 | 52-66285 |  | 400 | 49-9173-01
|  | 17037 | 17 | 34 | 52-66285 | 18.1 | 34 | 52-66292 |  | 450 | 49-9183-01
|  | 18148 | 18.1 | 34 | 52-66292 | 18.8 | 35 | 52-66301 |  | 500 | 49-9193-01
|  | 18797 | 18.8 | 35 | 52-66301 | 19.5 | 35 | 52-66305 |  | 600 | 49-9203-01
|  | 19467 | 19.5 | 35 | 52-66305 | 20.5 | 35 | 52-66312 |  | 800 | 49-9213-01
|  | 20464 | 20.5 | 35 | 52-66312 | 21.5 | 36 | 52-66319
|  | 21527 | 21.5 | 36 | 52-66319 | 22.4 | 36 | 52-66326
|  | 22449 | 22.4 | 36 | 52-66326 | 23.5 | 36 | 52-66332
|  | 23482 | 23.5 | 36 | 52-66332 | 24.5 | 37 | 52-66338
|  | 24531 | 24.5 | 37 | 52-66338 | 25.6 | 38 | 52-66344
|  | 25621 | 25.6 | 38 | 52-66344 | 26.5 | 38 | 52-66349
|  | 26528 | 26.5 | 38 | 52-66349 | 27.7 | 38 | 52-66356
|  | 27686 | 27.7 | 38 | 52-66356 | 29.2 | 38 | 52-66362
|  | 29157 | 29.2 | 38 | 52-66362 | 30 | 39 | 52-66367
|  | 29954 | 30 | 39 | 52-66367 | 31 | 39 | 52-66373
|  | 30976 | 31 | 39 | 52-66373 | 32.3 | 40 | 52-66379
|  | 32260 | 32.3 | 40 | 52-66379 | 33.6 | 40 | 52-66385
|  | 33565 | 33.6 | 40 | 52-66385 | 35 | 40 | 52-66391
|  | 34953 | 35 | 40 | 52-66391 | 36.3 | 42 | 52-66393
|  | 36336 | 36.3 | 42 | 52-66393 | 37.7 | 43 | 52-66398
|  | 37685 | 37.7 | 43 | 52-66398 | 38.6 | 44 | 52-66400
|  | 38607 | 38.6 | 44 | 52-66400 | 41 | 46 | 52-66407
|  | 40971 | 41 | 46 | 52-66407 | 45 | 49 | 52-66407H
|  | 45000 | 45 | 49 | 52-66407H | 45 | 49 | 52-66407H
Valve | Flow | Qty
Dim. | m³/h | Cartridges
DN
50 | 3,8 - 45,0 | 1
65 | 3,8 - 45,0 | 1
80 | 3,8 - 45,0 | 1
100 | 3,8 - 90,0 | 2
125 | 3,8 - 135,0 | 3
150 | 3,8 - 180,0 | 4
200 | 3,8 - 315,0 | 7
250 | 3,8 - 540,0 | 12
300 | 3,8 - 675,0 | 15
350 | 3,8 - 855,0 | 19
400 | 3,8 - 1.170,0 | 26
450 | 3,8 - 1.485,0 | 33
500 | 3,8 - 1.800,0 | 40
600 | 3,8 - 2.520,0 | 56
800 | 3,8 - 3.825,0 | 85

## EVA
Quick - CALC Frese EVA
Selection program Frese EVA Dynamic Balancing & Control Valve On/Off
|  | Input |  | CARTRIDGE SELECTION |  |  |  | Flow | Min. ΔP kPa | Min. ΔP kPa | Item no. | Item no. | Deviation
| Input Q = | 77 | (l/h) Flow | with selected Valve dimension (DN) |  |  |  | l/h | Cartridge | total valve | LP | HP
| ΔP range (kPa) | DN15-25 |  | Nearest higher Flow |  |  |  | 84 | 9 | 9 | 50-11260 | 49-11260 | 9.091%
| LP Low Press. | 7-350
| HP High Press. | 7-600 |  | Nearest lower Flow |  |  |  | 75 | 8 | 8 | 50-11230 | 49-11230 | -2.597%
Dimension Valve house DN ; Kvs = 3,0
| Input DN = | 32
Frese EVA with Plugs
| EVA F/F | Item no.
| 25 | 48-5805
Frese EVA with P/T plugs
| EVA F/F | Item no.
| 25 | 48-5802
|  |  |  | Actuator (NC) |  | Item no.
| Male/Male |  |  | 24 V On/Off |  | 48-5515
| EVA Basic | Item no. |  | 230 V On/Off |  | 48-5518
| 15 | 48-5806
| EVA | Berechnung nächst kleiner Volumenstrom |  |  |  |  | Berechnung nächst größer Volumenstrom |  |  |  |  | EVA Ventilgehäuse
| Ventil | Vol.- | Min. ΔP | Min. ΔP | Art.-Nr. | Art.-Nr. | Vol.- | Min. ΔP | Min. ΔP | Art.-Nr. | Art.-Nr. | Art.-Nr. | Art.-Nr.
| Dimension | Strom | Einsatz | Ges. Ventil | LP-Einsatz | HP-Einsatz | Strom | Einsatz | Ges. Ventil | LP-Einsatz | HP-Einsatz | EVA S | EVA DM
| DN | L/h | kPa | kPa | bis 3,5 bar | bis 6,0 bar | L/h | kPa | kPa | bis 3,5 bar | bis 6,0 bar | IG/IG | IG/IG
| 15 | 75 | 8 | 8 | 50-11230 | 49-11230 | 84 | 9 | 9 | 50-11260 | 49-11260 | 48-5803 | 48-5800
| 20 | 75 | 8 | 8 | 50-11230 | 49-11230 | 84 | 9 | 9 | 50-11260 | 49-11260 | 48-5804 | 48-5801
| 25 | 75 | 8 | 8 | 50-11230 | 49-11230 | 84 | 9 | 9 | 50-11260 | 49-11260 | 48-5805 | 48-5802
| EVA Basic | [10 empty] | EVA Basic
| 15 | 75 | 8 | 8 | 50-11230 | 49-11230 | 84 | 9 | 9 | 50-11260 | 49-11260 | 48-5806
| DN15-DN25 | [14 empty] | Gehäuse sind mit Stopfen, Druckmessnippel oder Füll- und Entleerungskugelhahn
| Kleiner |  |  |  |  | Grosser
| L/h | Min | Min DP To |  |  | L/h | Min | Min DP To | Vare nr. | [6 empty] | Der Regelbereich = S ….
|  | DP | Geh.+Eins. | LP | HP |  | DP | Geh+Ein | LP | HP
| 0 |  |  |  |  | 25 | 7 | 7 | 50-11150 | N/A
| 25 | 7 | 7 | 50-11150 | N/A | 36 | 7 | 7 | 50-11170 | N/A
| 36 | 7 | 7 | 50-11170 | N/A | 43 | 7 | 7 | 50-11190 | N/A
| 43 | 7 | 7 | 50-11190 | N/A | 55 | 7 | 7 | 50-11210 | 49-11210
| 55 | 7 | 7 | 50-11210 | 49-11210 | 75 | 8 | 8 | 50-11230 | 49-11230
| 75 | 8 | 8 | 50-11230 | 49-11230 | 84 | 9 | 9 | 50-11260 | 49-11260
| 84 | 9 | 9 | 50-11260 | 49-11260 | 104 | 10 | 10 | 50-11290 | 49-11290
| 104 | 10 | 10 | 50-11290 | 49-11290 | 114 | 10 | 10 | 50-11300 | 49-11300
| 114 | 10 | 10 | 50-11300 | 49-11300 | 129 | 11 | 11 | 50-11320 | 49-11320
| 129 | 11 | 11 | 50-11320 | 49-11320 | 154 | 11 | 11 | 50-11350 | 49-11350 |  |  |  | 50-33112 | 49-33112
| 154 | 11 | 11 | 50-11350 | 49-11350 | 175 | 12 | 12 | 50-11370 | 49-11370 |  |  |  | 50-33118 | 49-33118
| 175 | 12 | 12 | 50-11370 | 49-11370 | 204 | 12 | 12 | 50-11400 | 49-11400 |  |  |  | 50-33124 | 49-33124
| 204 | 12 | 12 | 50-11400 | 49-11400 | 241 | 12 | 13 | 50-11430 | 49-11430 |  |  |  | 50-33125 | 49-33125
| 241 | 12 | 13 | 50-11430 | 49-11430 | 279 | 12 | 13 | 50-11460 | 49-11460 |  |  |  | 50-33129 | 49-33129
| 279 | 12 | 13 | 50-11460 | 49-11460 | 320 | 13 | 14 | 50-11490 | 49-11490 |  |  |  | 50-33132 | 49-33132
| 320 | 13 | 14 | 50-11490 | 49-11490 | 350 | 13 | 14 | 50-11510 | 49-11510 |  |  |  | 50-33135 | 49-33135
| 350 | 13 | 14 | 50-11510 | 49-11510 | 400 | 13 | 15 | 50-11540 | 49-11540 |  |  |  | 50-33138 | 49-33138
| 400 | 13 | 15 | 50-11540 | 49-11540 | 477 | 14 | 17 | 50-11570 | 49-11570 |  |  |  | 50-33142 | 49-33142
| 477 | 14 | 17 | 50-11570 | 49-11570 | 545 | 14 | 17 | 50-11620 | 49-11620 |  |  |  | 50-33148 | 49-33148
| 545 | 14 | 17 | 50-11620 | 49-11620 | 615 | 14 | 18 | 50-11725 | 49-11725 |  |  |  | 50-33156 | 49-33156
| 615 | 14 | 18 | 50-11725 | 49-11725 | 670 | 14 | 19 | 50-11730 | 49-11730 |  |  |  | 50-33161 | 49-33161
| 670 | 14 | 19 | 50-11730 | 49-11730 | 736 | 14 | 20 | 50-11735 | 49-11735 |  |  |  | 50-33163 | 49-33163
| 736 | 14 | 20 | 50-11735 | 49-11735 | 799 | 16 | 23 | 50-11740 | 49-11740 |  |  |  | 50-44148 | 49-44148
| 799 | 16 | 23 | 50-11740 | 49-11740 | 870 | 19 | 27 | 50-11745 | 49-11745 |  |  |  | 50-44152 | 49-44152
| 870 | 19 | 27 | 50-11745 | 49-11745 | 936 | 21 | 31 | 50-11750 | 49-11750 |  |  |  | 50-44156 | 49-44156
| 936 | 21 | 31 | 50-11750 | 49-11750 | 1020 | 22 | 34 | 50-20700 | 49-20700 |  |  |  | 50-44164 | 49-44164
| 1020 | 22 | 34 | 50-20700 | 49-20700 | 1081 | 22 | 35 | 50-20740 | 49-20740 |  |  |  | 50-44168 | 49-44168
| 1081 | 22 | 35 | 50-20740 | 49-20740 | 1195 | 22 | 38 | 50-20770 | 49-20770 |  |  |  | 50-44173 | 49-44173
| 1195 | 22 | 38 | 50-20770 | 49-20770 | 1335 | 23 | 43 | 50-20820 | 49-20820 |  |  |  | 50-44176 | 49-44176
| 1335 | 23 | 43 | 50-20820 | 49-20820 | 1483 | 23 | 47 | 50-20860 | 49-20860 |  |  |  | 50-44182 | 49-44182
| 1483 | 23 | 47 | 50-20860 | 49-20860 | 1581 | 23 | 51 | 50-20880 | 49-20880 |  |  |  | 50-44191 | 49-44191
| 1581 | 23 | 51 | 50-20880 | 49-20880 | 1774 | 24 | 59 | 50-20920 | 49-20920 |  |  |  | 50-44194 | 49-44194
| 1774 | 24 | 59 | 50-20920 | 49-20920 | 1883 | 24 | 61 | 50-20940 | 49-20940 |  |  |  | 50-44200 | 49-44200
| 1883 | 24 | 61 | 50-20940 | 49-20940 | 2080 | 25 | 73 | 50-20990 | 49-20990 |  |  |  | 50-44205 | 49-44205
| 2080 | 25 | 73 | 50-20990 | 49-20990 | 2251 | 26 | 82 | 50-21030 | 49-21030 |  |  |  | 50-44211 | 49-44211
| 2251 | 26 | 82 | 50-21030 | 49-21030 | 2319 | 27 | 87 | 50-21060 | 49-21060 |  |  |  | 50-44217 | 49-44217
| 2319 | 27 | 87 | 50-21060 | 49-21060 | 2448 | 28 | 95 | 50-21090 | 49-21090 |  |  |  | 50-44222 | 49-44222
| 2448 | 28 | 95 | 50-21090 | 49-21090 | 2448 | 28 | 95 | 50-21090 | 49-21090 |  |  |  | 50-44229 | 49-44229
[14 empty] | 50-44235 | 49-44235
[14 empty] | 50-44241 | 49-44241
[14 empty] | 50-44248 | 49-44248
[14 empty] | 50-44250 | 49-44250
[14 empty] | 50-44262 | 49-44262
[14 empty] | 50-44262 | 49-44262
EVA
| Valve | Flow
Dimension
| DN | l/h
| 15 | 25-2448
| 20 | 25-2448
| 25 | 25-2448
EVA Basic
| 15 | 25-2448

## Frese OPTIMIZER
QUICK - CALC Frese OPTIMIZER
Control unit 4-pipe Heating/Cooling Systems
Input
Input dP = | 400 | (kPa) Differential pressure across valve
Flow cooling | 1000 | l/h
Flow heating | 500 | l/h
Dimension | Range |  | Calculation cooling |  | Calculation heating
| Flow l/h | Range ∆Pp (kPa) | Pre-set | Min. ∆P (kPa) | Pre-set
DN15 Low 5,0 | 65-370 | 14-400 | NOT POSSIBLE | NOT POSSIBLE | NOT POSSIBLE
DN15 High 5,0 | 220-1330 | 16-400 | 3.0261 | 20.682 | 50%
DN25L 5,5 High | 600-3609 | 17-400 | 1.052 | 17.4491 | 50%
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN
Type |  |  | X | Z | Kvs | Min | Max | Evaluering af Flow | Evaluering af Dp
DN15 Low 5,0 |  |  |  |  | 0.9 | 65 | 370 | UDEN FOR OMRÅDET | 400
DN15 High 5,0 |  |  |  |  | 2.7 | 220 | 1330 | 1000 | 400
DN25 |  |  |  |  | 7.5 | 600 | 3609 | 1000 | 400
Date 01-04-2014